## Slide 1: Multi-Sensor Fire Alarm
Eleazar Arnold – P2765566
ENG3000
Supervisor - Krishna Nama Manjunathan

## Slide 2: Introduction
A solar-powered multi-sensor indoor air monitoring device that alerts users in real time with a mobile app connected to an mqtt broker
Most homes use separate alarms (Heat, Smoke, CO), wasting energy and materials.
  My system combines them all and runs on renewable energy, supporting health, sustainability, and safety.

## Slide 3: Aims & Objectives
Objectives
  Combining multiple environmental sensors in one system
  Notify users via real-time mobile alerts
    Everyone has a phone, so this will be practical
  Reduce battery waste using solar + rechargeable LiPo
United Nations Goals Supported
  Affordable and clean energy
    Power the device with solar energy and rechargeable battery
  Climate action
    Reduce battery waste and greenhouse emissions
  Good health and well-being
    Notify users through a cross-platform mobile app (gives peace of mind as well)
    Support indoor air quality and fire safety

## Slide 4: System architecture
Esp32
  Reads sensor data
  Publishes to mqtt broker (HIVEMQ)
  Runs on solar power
  Arduino ide to program the esp32
Sensor peripherals
  DHT11
  BMP280
  MQ-7
  GP2Y101OAU
Power system
  MT3608
  TP4056
  8 SOLAR CELLS FORM SUMIYA
  LiPo BATTERY
App – Flutter
  Decoding and creating widgets
  Going into the source code
Communication
  Firebase (FCM)
  Mqtt functions
  Json payloads
Sensors/Peripherals:
DHT
MQ7
BMP280
GP2Y1014
ESP32
MQTT Broker
(HIVEMQ)
Mobile App
Battery
Solar Cells
Firebase Alert (FCM)

## Slide 5: Hardware
ALL ON A STRIPBOARD FOR NOW
Designed on KICAD (PCB is ready for fabrication)
ESP32 – chosen for Wi-Fi, small, cheap, and reliable
Sensor peripherals
  DHT11
  BMP280 (connected through i2c)
  MQ-7
  GP2Y1010AU
Power system
  MT3608
  TP4056
  8 SOLAR CELLS FORM SUNMIYA (changed topology from report submission) 
  LiPo BATTERY

## Slide 6: Software
ESP32
  SENSOR READINGS ARE TURNED INTO JSON PAYLOADS MADE IN THE ESP32 PROGRAM(C++), ARE SENT TO THE HIVEMQ BROKER.
    JSON (JavaScript Object Notation)
Google Firebase
  App backend building service in my case, I will use it for cloud messaging
  Used as a database, can also do things such graph data and analyse
HiveMQ
  Private broker that holds payloads
  During testing, the broker I used was test.mosquitto.org
Flutter (also made by Google in 2017)
  Firebase messaging dependency(library) needs to be added
  Going into the source code to enable push notifications: in-app and when the app is in the background
  Mqtt functions are required in the dependencies/libraries
  Local push notification library has to too
    FLUTTER APP IS SUBSCRIBED TO THE BROKER AND DECODES THE JSON PAYLOAD AND DISPLAYS EACH INDIVIDUAL SENSOR READINGS ON THE WIDGETS
  Decoding JSON payloads and creating widgets
  WHEN A READING HAS BREACHED ITS THRESHOLD (EG: SMOKE = HIGH), THEN THE APP WILL SEND A HIGH-PRIORITY NOTIFICATION

## Slide 7: Demonstration
Show how it works (restart phone/app if you have to)

## Slide 8: Testing and Results
Much troubleshooting, especially with software!
Costs were high!
1. Solar Cells + LiPo Battery and Modules
  I measured output voltage by measuring the potential difference across the positive bus and negative bus of the solar cells, as they’re connected in parallel
  In low light, the topology generates about 0.8 volts; in normal light, it's about 4 volts. In high light, it can go up to 6 volts.
  (include voltage log screenshot or show in demo)
2. Sensor Behavior
  DHT11: The values of temperature and humidity were consistent with the room
    Ended up destroying the ESP32 voltage regulator and DHT11 module, due to MT3608 startup (power surge)
  MQ-7: Responds to carbon monoxide levels in the air and also reacts to nearby combustion
  BMP280: It has Stable pressure values and is very consistent.
  GP2Y1014: Previously worked independently but has not been integrated into the system peripherals
    Optical smoke sensor kept on failing
3. Full System
  Data correctly sent via MQTT to the App
  JSON formatted and was sent correctly with no issues
  Push notifications were triggered successfully

## Slide 9: Evaluation and Conclusion
Positives:
Real-time notifications
Runs on solar (renewable) energy
Cross-platform mobile app (Flutter)
Easy to upgrade, such as reprogramming esp32 or adding more peripherals
Negatives:
GP2Y1010AU0F failed during testing
Cloud-dependent (no offline alerts) and no notifications when app is terminated and not running in the background
No enclosure, so the components are exposed at the moment
Linked to the point above, the PCB wasn't fabricated in time (used stripboard instead)
Deep sleep mode wasn’t implemented. It could have been a GPIO pin acting as a voltmeter to the TP4056 battery terminal. When it reaches below a certain threshold, it activates sleep mode. That is only measuring smoke, heat and carbon monoxide,
I haven’t coded it for iOS, and at the moment, the app is privately downloaded from my PC. It is also not natively coded for Android.
Also, the device isn’t completed, such as he real PCB or the real body
Conclusion:
The system meets original aims:
  low-cost, multi-sensor, solar-powered, mobile-integrated
Successfully implemented real-time monitoring and push notifications
Enabling notifications was the trickiest part.
Future Work:
Build final chassis (possibly from heat resistant material)
Finish PCB and solder all components
Add a local alert system (buzzer and reset button)
Reduce the cost of components
Add a different smoke sensor (as GP2Y1010AU0F kept on failing)